#

#

C A S E:    GAS FURNACE  - THERMALLY ACTIVATED DAMPER                   DATE: 02-02-1994

=========================================================================================================================

TIME    TIME(IN #   FURNACE    DILUTION  HOT WATER   CHIMNEY    INC. ENVEL  ENVELOPE   FURNACE    FURNACE    MIXING     DHW BRANCH  MEAN FLUE  GAS EXIT   MEAN FLUE  INSTANT.   FLUE FILM   FLUE     DRAFT       CONDENSATION

(s)    FURN. T-C)  FLOW(L/s)  FLOW(L/s) BRANCH(L/s) FLOW(L/s)  FLOW(L/s)   PRES DROP  HT-EX TEMP EXIT TEMP  TEMP(C)    TEMP (C)    GAS TEMP   TEMP (C)   LINER TEMP EFFICIENCY LOSS COEFF FRICTION  AT ELEMENT  AT ELEMENT

600.6     12.91         5.4       13.9       0.0        19.2       17.9       -0.4       21.0       21.2       20.4      20.0        20.0       17.5       19.3        0.2        9.0        3.9       -1.4      ----

WARNING: INSUFFICIENT FURNACE AIR FLOW -- INCOMPLETE COMBUSTION

601.2     12.92        20.7      -14.8       0.0         5.8        5.4       -0.1       21.0       21.2       20.3      20.0        20.1       18.2       19.3        0.2       11.9        3.5       -3.6      ----

601.8     12.93        19.3      -13.3       0.0         5.8        5.4       -0.1       21.2       22.8       22.8      20.0        20.2       18.2       19.3        0.3        9.0        3.5       -3.6      ----

602.3     12.94        19.6      -13.4       0.0         5.9        5.5       -0.1       21.5       25.8       25.8      20.0        20.3       18.0       19.3        0.4        9.0        3.5       -3.7      ----

602.8     12.95        19.9      -13.3       0.0         5.9        5.5       -0.1       22.0       29.6       29.6      20.0        20.5       17.9       19.3        0.5        9.0        3.5       -3.8      ----

603.3     12.96        20.1      -13.3       0.0         5.9        5.5       -0.1       22.5       33.7       33.7      20.0        20.8       17.8       19.3        0.6        9.0        3.5       -3.9      ----

603.8     12.97        20.3      -13.2       0.0         6.0        5.6       -0.1       23.1       38.0       38.0      20.0        21.2       17.7       19.3        0.8        9.0        3.5       -4.0      ----

604.3     12.98        20.6      -13.1       0.0         6.1        5.7       -0.1       23.8       42.3       42.3      20.0        21.7       17.7       19.3        0.9        9.0        3.5       -4.2      ----

604.8     12.99        20.7      -14.3       0.0         4.6        4.3       -0.1       24.4       46.4       46.4      20.0        22.2       17.6       19.3        1.1        9.0        4.8       -2.5      ----

605.3     13.00        20.9      -14.5       0.0         4.4        4.1       -0.0       25.0       50.3       50.3      20.0        22.6       17.5       19.3        1.3        9.0        5.4       -2.1      ----

625.0     13.43        24.9       -5.1       0.0        15.2       12.9       -0.2       51.7      111.7      111.7      20.0        56.5       31.3       22.4        7.9       10.9        7.6       -4.9      ----

650.0     13.96        26.5        0.8       0.0        22.6       18.2       -0.4       81.6      141.6      137.1      20.0        76.2       46.0       33.0       15.3       14.4        5.8       -7.0      ----

675.0     14.51        27.9        3.4       0.0        26.4       20.5       -0.4      108.3      167.8      145.1      20.0        87.9       57.9       45.3       21.9       15.9        5.4       -7.9      ----

700.0     15.04        29.1        5.4       0.0        29.6       22.3       -0.5      129.2      189.5      151.0      20.0        97.8       68.6       56.6       46.7       17.0        5.1       -8.5      ----

725.0     15.58        29.8        6.7       0.0        31.7       23.4       -0.5      141.9      202.2      153.7      20.0       105.1       77.7       66.7       52.1       17.7        4.9       -9.0      ----

750.0     16.11        30.4        7.7       0.0        33.5       24.3       -0.6      152.3      212.4      155.7      20.0       111.2       85.3       75.2       56.6       18.2        4.8       -9.3      ----

775.0     16.65        30.9        8.5       0.0        35.0       24.9       -0.6      160.7      220.7      157.4      20.0       116.2       91.8       82.5       60.2       18.6        4.7       -9.5      ----

800.0     17.19        31.2        9.1       0.0        36.2       25.5       -0.6      167.6      227.5      158.7      20.0       120.4       97.2       88.6       63.1       19.0        4.7       -9.7      ----

825.0     17.73        31.5        9.6       0.0        37.2       25.9       -0.6      173.2      233.0      159.7      20.0       123.9      101.8       93.8       65.5       19.2        4.6       -9.8      ----

850.0     18.26        31.8       10.0       0.0        38.0       26.3       -0.6      177.8      237.5      160.6      20.0       126.9      105.7       98.3       67.5       19.4        4.6       -9.9      ----

875.0     18.80        32.0       10.3       0.0        38.7       26.6       -0.6      181.5      241.1      161.2      20.0       129.4      109.1      102.1       69.1       19.6        4.6      -10.0      ----

900.0     19.34        32.1       10.6       0.0        39.3       26.8       -0.6      184.5      244.1      161.7      20.0       131.5      111.9      105.4       70.4       19.8        4.5      -10.0      ----

925.0     19.88        32.3       10.8       0.0        39.8       27.0       -0.6      187.0      246.6      162.1      20.0       133.4      114.4      108.3       71.4       19.9        4.5      -10.1      ----

950.0     20.41        32.4       11.0       0.0        40.2       27.2       -0.7      189.0      248.5      162.4      20.0       134.9      116.5      110.7       72.3       20.0        4.5      -10.1      ----

975.0     20.95        32.5       11.2       0.0        40.6       27.4       -0.7      190.7      250.2      162.6      20.0       136.2      118.3      112.8       73.0       20.1        4.5      -10.2      ----

1000.0     21.48        32.5       11.3       0.0        40.9       27.5       -0.7      192.0      251.5      162.8      20.0       137.4      119.9      114.7       73.6       20.1        4.5      -10.2      ----

1025.0     22.02        32.6       11.4       0.0        41.1       27.6       -0.7      193.1      252.6      162.9      20.0       138.3      121.3      116.3       74.1       20.2        4.5      -10.2      ----

1050.0     22.56        32.7       11.5       0.0        41.3       27.6       -0.7      194.0      253.4      163.0      20.0       139.2      122.5      117.7       74.4       20.2        4.5      -10.2      ----

1075.0     23.10        32.7       11.6       0.0        41.5       27.7       -0.7      194.8      254.1      163.1      20.0       139.9      123.5      118.9       74.8       20.3        4.5      -10.3      ----

1100.0     23.64        32.7       11.6       0.0        41.7       27.8       -0.7      195.3      254.7      163.1      20.0       140.5      124.4      119.9       75.0       20.3        4.5      -10.3      ----

1125.0     24.17        32.8       11.7       0.0        41.8       27.8       -0.7      195.8      255.2      163.2      20.0       141.0      125.1      120.8       75.2       20.3        4.4      -10.3      ----

1150.0     24.71        32.8       11.7       0.0        41.9       27.9       -0.7      196.2      255.6      163.2      20.0       141.5      125.8      121.6       75.4       20.4        4.4      -10.3      ----

1175.0     25.25        32.8       11.8       0.0        42.0       27.9       -0.7      196.6      255.9      163.2      20.0       141.9      126.4      122.3       75.5       20.4        4.4      -10.3      ----

1200.0     25.79        32.8       11.8       0.0        42.1       27.9       -0.7      196.8      256.2      163.2      20.0       142.2      126.9      122.9       75.6       20.4        4.4      -10.3      ----

PHYSICAL CHARACTERISTICS OF THE SYSTEM

--------------------------------------

<--------------------F L U E--------------------> <--------E N V E L O P E------><--DRAFT HOOD INLET-> <---------------------F U R N A C E----------------------->

1        2        3        4        5        6        7        8        9       10       11       12       13       14       15       16       17       18       19

DISTANCE->DATUM (M)        0.00     0.00     0.00     8.92     8.92     9.18     0.00     3.65     3.65     9.18     9.18     9.18     9.18     9.90     9.90     9.90     8.97     8.97     9.18

AREA OF OPENING (M2)      0.000    0.013    0.013    0.013    0.013    0.000    0.000    0.000    0.000    0.000    0.040    0.000    0.000    0.000    0.040    1.000    1.000    0.011    0.000

K FACTOR NORMAL             0.0      1.0      1.5      1.4      0.5      0.0      0.0      0.0      0.0      0.0      4.0      0.0      0.0      0.0      3.0      0.0      0.0      2.0      0.0

TIME =   1200.1 SECONDS

===============================

TEMPERATURES OF THE FLUE GAS, LINER, AND STRUCTURE

--------------------------------------------------------

FP 1    FP 2     F 3     F 4     F 5     F 6     F 7     F 8     F 9    F 10

FLUE GAS TEMP (C)       158.6   153.9   150.4   147.0   143.6   140.3   137.0   133.9   130.3   126.9

INNER LINER    (C)      135.1   130.4   131.4   128.3   125.3   122.4   119.5   116.7   111.3   108.3

INSUL OR STRUCT (C)      88.3    85.0    73.3    71.6    70.0    68.4    66.8    65.3    54.4    52.8

OUTER STRUCTURE(C)       22.7    22.5    22.2    22.1    22.0    21.9    21.8    21.7     5.7     5.6

SURROUNDING (DEG C)      20.0    20.0    20.0    20.0    20.0    20.0    20.0    20.0     0.0     0.0

CONDENSING TIME (%)       0.0     0.0     0.0     0.0     0.0     0.0     0.0     0.0     0.0     0.0

THE MASSFLOW SYSTEM PARAMETERS

-------------------------------

<--------------------F L U E--------------------> <--------E N V E L O P E------><--DRAFT HOOD INLET-> <---------------------F U R N A C E----------------------->

1        2        3        4        5        6        7        8        9       10       11       12       13       14       15       16       17       18       19

TEMPERATURE (DEG C)        0.0    126.9    138.5    158.6    163.2    163.2      0.0      0.0     20.0     20.0     20.0    163.2     20.0     20.0     20.0   1240.3    256.2    256.2    163.2

DENSITY (KG/M3)            1.29     0.88     0.86     0.82     0.81     0.81     1.29     1.29     1.21     1.21     1.21     0.81     1.21     1.21     1.21     0.23     0.67     0.67     0.81

MASS FLOW (KG/S)          0.036    0.036    0.036    0.036    0.036    0.036    0.036    0.036    0.036    0.014    0.014    0.014    0.022    0.022    0.021    0.022    0.022    0.022    0.022

VOLUME FLOW (M3/S)        0.028    0.041    0.042    0.044    0.045    0.045    0.028    0.028    0.030    0.012    0.012    0.018    0.018    0.018    0.018    0.094    0.033    0.033    0.027

FLOW VELOCITY (M/S)       0.00     0.00     0.00     0.00     0.00     0.00     0.00     0.00     0.00     0.00    -0.08     0.00     0.00     0.00     0.00     0.00     0.00     0.00     0.00

PRESSURE PARAMETERS OF THE FLOW SYSTEMS

---------------------------------------

NET BUOYANCY     WIND EFFECT    ENVELOPE LOSS   FRICTION LOSS   NET DRIVING    FURN BUOYANCY    INLET DROP     OUTLET DROP     NET FURNACE     DILUTION PORT    DRAFT INDUCER   DHW INDUCED   DHW BUOYANCY

34.997           2.913          -0.679         -37.020           0.210           6.089          -0.354          -5.945          -0.211          -0.210           0.000           0.000           0.000

#

S U M M A R Y   T A B L E

-------------------------

OUTDOOR TEMPERATURE     =      0 C

INDOOR  TEMPERATURE     =     20 C

STANDBY FIRING RATE     =      0 W

FULL FIRING RATE        =  29300 W

INSTANT.  EFFICIENCY    =   75.6 %

WIND SPEED & PRESSURE         SPEED     PRESSURE COEFFICIENTS

COEFFICIENTS:                 (M/S)      CHIM TOP    INSIDE HOUSE

---------------------          -----     --------    ------------

HORIZONTAL COMPONENT           3.0       0.50        0.00

VERT. COMPONENT (+VE UP)       0.0       1.00

FLOW RATES:                    L/S      KG/S

-----------                    ---      ----

FUEL FLOW                      0.000    0.000

FURNACE OUTLET FLOW           32.8      0.022 ( 123 % EXCESS AIR)

DILUTION FLOW INTO HOOD       11.7      0.014

FLUE INLET FLOW               44.6      0.036 ( 274 % EXCESS AIR)

FAN FLOW                       0.0      0.000

FIREPLACE FLOW                 0.0      0.000

INCREMENTAL ENVELOPE FLOW     27.9      0.036  (AT OUTDOOR TEMPERATURE)

INDUCED PRESSURE DROP ACROSS THE ENVELOPE = -0.7 Pa

TEMPERATURES:

---------------

FURNACE FLAME TEMPERATURE  = 1240.  C

FURNACE EXIT  TEMPERATURE  =  256.2 C

FLUE GAS T. AFTER DILUTION =  163.2 C

MEAN FLUE GAS TEMPERATURE =   142.2 C

MEAN FLUE LINER TEMPERATURE=  122.9 C

THERMAL PROPERTIES OF FURNACE & CHIMNEY

---------------------------------------

HEAT CAPACITY OF FURNACE HEAT EXCHANGER             = 17500.  W.S/C

DESIGN HEAT TRANSFER RATE FROM GAS TO FURN HEAT-EXCH=   376.  W/C

FURNACE HEAT TRANSFER TIME CONSTANT                 =    47.  SECS

FURNACE HEAT TRANSPORT TIME CONSTANT (FINAL CONDIT) =    18.1 SECS

AT THE BASE OF THE CHIMNEY:                        FLUE GAS       LINER         SLEEVE      STRUCTURE

--------------------------                         --------       -----         ------      ---------

HEAT TRANSFER COEFF. 'U' (W/(M2.C))                20.406         5.850         5.280         7.230

ELEMENTAL SURFACE AREA 'A' (M2)                     0.339         0.374         0.428         0.863

ELEMENTAL MASS 'M' (KG)                             0.008         0.307         1.004        16.353

HEAT CAPACITY OF MATERIALS 'CP'  (W.S/KG.C)      1035.0         896.0         500.0        1080.0

HEAT TRANSFER TIME CONSTANTS-OUT (S)                1.2         125.9         222.4        2832.2

HEAT TRANSFER TIME CONSTANTS-IN  (S)                             39.9         229.5        7824.4

ENVELOPE CHARACTERISTICS:       WITHOUT     WITH

------------------------        AIR INTAKE  AIR INTAKE (IF ANY)

----------  ----------

FLOW COEFFICIENT (M3/(S.PA^N) = 0.0307      0.0369

FLOW EXPONENT    (--)         = 0.720       0.720

LOCATION OF VCL BELOW CHIM TOP= 2.80        3.65(m)

HOT WATER HEATER SPECS. FOR A SHARED FLUE ARRANGEMENT

-----------------------------------------------------

-----  NONE  -----